## VOORBLAD (2)
Haltepalen
SPIE Belgium
Keiberg Park
Excelsiorlaan, 16
1930 Zaventem
Tel: +32 (0)2 729 61 11
Tel: +32 (0)2 729 61 61
VERMOGENBILAN
B | 30/04/208 | [5 empty] | VIA
A | 2008-10-27 |  | Eerste uitgave |  |  |  | VIA
Rev | Datum | Stat, | Beschrijving |  |  |  | Tek, | Nag, | Goe,
Datum: |  | Getekend: | VIA | Nagezien: |  | Goedgekeurd |  | Status | PRE
582001-ELE-CAL-130
Schaal: | NVT | Plan Nr: | [5 empty] | Folio: 01 | Rev: B

## Sheet1 (2)
582001-ELE-CAL-001 |  |  | Date: | 2009-04-30
Vermorgen bilan |  |  | Author: | VIA
1. Maximum Power requirement
|  | Description |  | Quantity | Hours of use per day [h] | "Mechanical" Power | Efficiency | cos f | Active Power P [W] | Apparent Power S [VA] | Reactive Power Q [Var] | Voltage U [V] | Current I [A] | Daily Energy requirement [Wh]
[8 empty] | 0.95591 | 606.4661 | 634.4365 | 186.3023 | 230 | 1.9505 | 14855.2545
|  | DC equipement | [6 empty] | 221.8 | 221.8 | 0 | 24 | 9.2417
| Moxa | Embedded computer |  | 1 | 24 | 4 | 100% | 1 | 4 | 4 | 0 | 24 | 0.16667 | 96
| eDbox | Gprs Modem |  | 1 | 24 | 10 | 100% | 1 | 10 | 10 | 0 | 24 | 0.41667 | 240
| Weidmueller | Relais de sortie |  | 7 | 24 | 2.4 | 100% | 1 | 2.4 | 2.4 | 0 | 24 | 0.1 | 57.6
| Abaccus | TRANSFLECTIEF TFT-SCHERM |  | 1 | 20 | 150 | 100% | 1 | 150 | 150 | 0 | 24 | 6.25 | 3000
| Pelko | Verluchting scherm |  | 2 | 24 | 10.5 | 100% | 1 | 10.5 | 10.5 | 0 | 24 | 0.4375 | 252
| Diagnose Modules | Diagnose Modules |  | 2 | 24 | 10 | 100% | 1 | 10 | 10 | 0 | 24 | 0.41667 | 240
|  | AC equipement | [5 empty] | 0.9 | 384.6661 | 427.4068 | 186.3023 | 230 | 1.8583
| Audio XL | Ampli Audio |  | 1 | 20 | 40 | 100% | 0.9 | 28.2843 | 31.427 | 13.6987 | 230 | 0.13664 | 628.5394
| Sarel | Verluchting kast |  | 1 | 24 | 24 | 100% | 0.9 | 16.9706 | 18.8562 | 8.2192 | 230 | 0.081983 | 452.5483
| DBK | Verwarming (kast) |  | 4 | 24 | 60 | 100% | 0.9 | 42.4264 | 47.1405 | 20.548 | 230 | 0.20496 | 1131.3708
| DBK | Verwarming (scherm) |  | 4 | 24 | 60 | 100% | 0.9 | 42.4264 | 47.1405 | 20.548 | 230 | 0.20496 | 1131.3708
2. Power requirement for low temperature (heating on)
|  | Description |  | Quantity | Hours of use per day [h] | "Mechanical" Power | Efficiency | cos f | Active Power P [W] | Apparent Power S [VA] | Reactive Power Q [Var] | Voltage U [V] | Current I [A] | Daily Energy requirement [Wh]
[8 empty] | 0.95428 | 568.4955 | 595.7355 | 178.0831 | 230 | 1.8315 | 13898.7062
|  | DC equipement | [6 empty] | 200.8 | 200.8 | 0 | 24 | 8.3667
| Moxa | Embedded computer |  | 1 | 24 | 4 | 100% | 1 | 4 | 4 | 0 | 24 | 0.16667 | 96
| eDbox | Gprs Modem |  | 1 | 24 | 10 | 100% | 1 | 10 | 10 | 0 | 24 | 0.41667 | 240
| Weidmueller | Relais de sortie |  | 7 | 24 | 2.4 | 100% | 1 | 2.4 | 2.4 | 0 | 24 | 0.1 | 57.6
| Abaccus | TRANSFLECTIEF TFT-SCHERM |  | 1 | 20 | 150 | 100% | 1 | 150 | 150 | 0 | 24 | 6.25 | 3000
| Pelko | Verluchting scherm |  | 0 | 24 | 10.5 | 100% | 1 | 10.5 | 10.5 | 0 | 24 | 0.4375 | 252
| Diagnose Modules | Diagnose Modules |  | 2 | 24 | 10 | 100% | 1 | 10 | 10 | 0 | 24 | 0.41667 | 240
|  | AC equipement | [5 empty] | 0.9 | 367.6955 | 408.5506 | 178.0831 | 230 | 1.7763
| Audio XL | Ampli Audio |  | 1 | 20 | 40 | 100% | 0.9 | 28.2843 | 31.427 | 13.6987 | 230 | 0.13664 | 628.5394
| Sarel | Verluchting kast |  | 0 | 24 | 24 | 100% | 0.9 | 16.9706 | 18.8562 | 8.2192 | 230 | 0.081983 | 452.5483
| DBK | Verwarming (kast) |  | 4 | 24 | 60 | 100% | 0.9 | 42.4264 | 47.1405 | 20.548 | 230 | 0.20496 | 1131.3708
| DBK | Verwarming (scherm) |  | 4 | 24 | 60 | 100% | 0.9 | 42.4264 | 47.1405 | 20.548 | 230 | 0.20496 | 1131.3708
3. Power requirement for high temperature (Cooling on)
|  | Description |  | Quantity | Hours of use per day [h] | "Mechanical" Power | Efficiency | cos f | Active Power P [W] | Apparent Power S [VA] | Reactive Power Q [Var] | Voltage U [V] | Current I [A] | Daily Energy requirement [Wh]
[8 empty] | 0.99665 | 267.0548 | 267.9528 | 21.9179 | 230 | 0.82379 | 5804.2877
|  | DC equipement | [6 empty] | 221.8 | 221.8 | 0 | 24 | 9.2417
| Moxa | Embedded computer |  | 1 | 24 | 4 | 100% | 1 | 4 | 4 | 0 | 24 | 0.16667 | 96
| eDbox | Gprs Modem |  | 1 | 24 | 10 | 100% | 1 | 10 | 10 | 0 | 24 | 0.41667 | 240
| Weidmueller | Relais de sortie |  | 7 | 24 | 2.4 | 100% | 1 | 2.4 | 2.4 | 0 | 24 | 0.1 | 57.6
| Abaccus | TRANSFLECTIEF TFT-SCHERM |  | 1 | 20 | 150 | 100% | 1 | 150 | 150 | 0 | 24 | 6.25 | 3000
| Pelko | Verluchting scherm |  | 2 | 24 | 10.5 | 100% | 1 | 10.5 | 10.5 | 0 | 24 | 0.4375 | 252
| Diagnose Modules | Diagnose Modules |  | 2 | 24 | 10 | 100% | 1 | 10 | 10 | 0 | 24 | 0.41667 | 240
|  | AC equipement | [5 empty] | 0.9 | 45.2548 | 50.2831 | 21.9179 | 230 | 0.21862
| Audio XL | Ampli Audio |  | 1 | 20 | 40 | 100% | 0.9 | 28.2843 | 31.427 | 13.6987 | 230 | 0.13664 | 628.5394
| Sarel | Verluchting kast |  | 1 | 24 | 24 | 100% | 0.9 | 16.9706 | 18.8562 | 8.2192 | 230 | 0.081983 | 452.5483
| DBK | Verwarming (kast) |  | 0 | 24 | 60 | 100% | 0.9 | 42.4264 | 47.1405 | 20.548 | 230 | 0.20496 | 1131.3708
| DBK | Verwarming (scherm) |  | 0 | 24 | 60 | 100% | 0.9 | 42.4264 | 47.1405 | 20.548 | 230 | 0.20496 | 1131.3708
4. Power requirement for "normal" temperature (no heating, no cooling)
|  | Description |  | Quantity | Hours of use per day [h] | "Mechanical" Power | Efficiency | cos f | Active Power P [W] | Apparent Power S [VA] | Reactive Power Q [Var] | Voltage U [V] | Current I [A] | Daily Energy requirement [Wh]
[8 empty] | 0.99822 | 229.0843 | 229.4935 | 13.6987 | 230 | 0.70555 | 4847.7394
|  | DC equipement | [6 empty] | 200.8 | 200.8 | 0 | 24 | 8.3667
| Moxa | Embedded computer |  | 1 | 24 | 4 | 100% | 1 | 4 | 4 | 0 | 24 | 0.16667 | 96
| eDbox | Gprs Modem |  | 1 | 24 | 10 | 100% | 1 | 10 | 10 | 0 | 24 | 0.41667 | 240
| Weidmueller | Relais de sortie |  | 7 | 24 | 2.4 | 100% | 1 | 2.4 | 2.4 | 0 | 24 | 0.1 | 57.6
| Abaccus | TRANSFLECTIEF TFT-SCHERM |  | 1 | 20 | 150 | 100% | 1 | 150 | 150 | 0 | 24 | 6.25 | 3000
| Pelko | Verluchting scherm |  | 0 | 24 | 10.5 | 100% | 1 | 10.5 | 10.5 | 0 | 24 | 0.4375 | 252
| Diagnose Modules | Diagnose Modules |  | 2 | 24 | 10 | 100% | 1 | 10 | 10 | 0 | 24 | 0.41667 | 240
|  | AC equipement | [5 empty] | 0.9 | 28.2843 | 31.427 | 13.6987 | 230 | 0.13664
| Audio XL | Ampli Audio |  | 1 | 20 | 40 | 100% | 0.9 | 28.2843 | 31.427 | 13.6987 | 230 | 0.13664 | 628.5394
| Sarel | Verluchting kast |  | 0 | 24 | 24 | 100% | 0.9 | 16.9706 | 18.8562 | 8.2192 | 230 | 0.081983 | 452.5483
| DBK | Verwarming (kast) |  | 0 | 24 | 60 | 100% | 0.9 | 42.4264 | 47.1405 | 20.548 | 230 | 0.20496 | 1131.3708
| DBK | Verwarming (scherm) |  | 0 | 24 | 60 | 100% | 0.9 | 42.4264 | 47.1405 | 20.548 | 230 | 0.20496 | 1131.3708